## PROJECT
MEP CALCULATION WORKBOOK
Project Metadata
Project Name | 18 Units Saint-Côme
Project Number | APH-2024-018
Project Type | APH | APH, Commercial, Industrial, Renovation, Healthcare
Client
Architect
Address | Saint-Côme, QC
Phase | Coordination | Coordination, Calculation, Drawing, Construction
Disciplines | Mechanical, Electrical, Plumbing
Has Kitchen/Commercial | No | Yes, No
Has Garage | No | Yes, No
Energy Compliance | Yes | Yes, No
Applicable Codes | Quebec, Canada, CSA | Quebec, Canada, CSA, ASHRAE
Last Modified | 2026-06-04 14:27

## ASSUMPTIONS
Parameter | Value | Unit | Notes | Status
Outdoor Design Temp (Summer) | 30 | °C | ASHRAE 1%
Outdoor Design Temp (Winter) | -25 | °C | ASHRAE 99%
Indoor Design Temp (Conditioned) | 22 | °C | ±2°C tolerance
Indoor Design Temp (Unconditioned) | 10 | °C | Min
Occupancy Type | Residential |  | Multi-unit
Occupant Density | 25 | m²/person | Per unit
Ventilation Rate | 7.5 | L/s/person | ASHRAE 62.1
Lighting Power Density | 5 | W/m² | Residential
Equipment Power Density | 5 | W/m² | Residential
Infiltration Rate | 0.25 | ACH | Typical
Ceiling Height | 2.44 | m | Floor to floor
Window-to-Wall Ratio | 0.25 |  | Estimated
Glazing U-Value | 1.8 | W/m²·K | Typical
Wall R-Value | 4.2 | RSI
Roof R-Value | 5.6 | RSI

## HVAC
ZONE LOAD SUMMARY
Zone ID | Area (m²) | Cooling (kW) | Heating (kW) | Ventilation (L/s) | Supply CFM | Return CFM | Exhaust CFM | Status
Unit-101 | 85 | 4.2 | 3.8 | 25 | 210 | 190 | 50
Unit-102 | 85 | 4.2 | 3.8 | 25 | 210 | 190 | 50
Unit-103 | 85 | 4.2 | 3.8 | 25 | 210 | 190 | 50
Unit-201 | 85 | 4.2 | 3.8 | 25 | 210 | 190 | 50
Unit-202 | 85 | 4.2 | 3.8 | 25 | 210 | 190 | 50
Unit-203 | 85 | 4.2 | 3.8 | 25 | 210 | 190 | 50
Corridor-1 | 45 | 1.5 | 1.2 | 15 | 75 | 75 | 0
Corridor-2 | 45 | 1.5 | 1.2 | 15 | 75 | 75 | 0
TOTALS
DUCT SIZING
Duct ID | Serves | CFM | Velocity (fpm) | Diam. (in) | Width (in) | Height (in) | ΔP (in.wg/100ft) | Status
M-001 | Units 1xx Supply | 630 | 900 | 14 |  |  | 0.08
M-002 | Units 2xx Supply | 630 | 900 | 14 |  |  | 0.08
M-003 | Corridors Supply | 150 | 500 | 10 |  |  | 0.04
M-R01 | Units 1xx Return | 570 | 800 | 14 |  |  | 0.06
M-R02 | Units 2xx Return | 570 | 800 | 14 |  |  | 0.06
M-E01 | Bath Exhaust | 100 | 600 | 8 |  |  | 0.05
M-E02 | Bath Exhaust | 100 | 600 | 8 |  |  | 0.05
EQUIPMENT SELECTION
Tag | Description | Model | Capacity | ESP (in.wg) | Electrical | Location | Status
RTU-1 | Rooftop Unit - Units 1xx | Trane Precedent 7.5T | 7.5 ton / 1500 CFM | 0.50 | 208/3/60 25A | Roof Zone A
RTU-2 | Rooftop Unit - Units 2xx | Trane Precedent 7.5T | 7.5 ton / 1500 CFM | 0.50 | 208/3/60 25A | Roof Zone B
ERV-1 | Energy Recovery Ventilator | Lifebreath 1200 | 1200 CFM | 0.75 | 120/1/60 8A | Mech Room 1
EF-1 | Bath Exhaust Fan | Fantech RE 6XL | 200 CFM | 0.25 | 120/1/60 3A | Roof

## PLUMBING
PLUMBING — FIXTURE & PIPE SCHEDULE
Fixture | Qty per Unit | Total Qty | FU Cold | FU Hot | Pipe Size Cold | Pipe Size Hot | Drain Size | Vent Size | Notes
Water Closet | 1 | 18 | 2.5 | 0 | 3/4" |  | 3" | 2"
Lavatory | 1 | 18 | 1 | 1 | 1/2" | 1/2" | 1-1/2" | 1-1/2"
Bathtub/Shower | 1 | 18 | 1.5 | 1.5 | 1/2" | 1/2" | 2" | 1-1/2"
Kitchen Sink | 1 | 18 | 1.5 | 1.5 | 1/2" | 1/2" | 1-1/2" | 1-1/2"
Washing Machine | 0.5 | 9 | 2 | 2 | 1/2" | 1/2" | 2" | 1-1/2" | Shared per 2 units
WATER HEATER
Tag | Type | Capacity | Recovery | Fuel | Location | Notes
WH-1 | Electric | 270 L (71 gal) | 150 L/h | Electric 240/1/60 | Mech Room | Serves Units 1xx
WH-2 | Electric | 270 L (71 gal) | 150 L/h | Electric 240/1/60 | Mech Room | Serves Units 2xx

## ELECTRICAL
ELECTRICAL — PANEL SCHEDULE
Panel ID | Voltage | Bus Rating (A) | Connected Load (kW) | Demand Factor | Demand Load (kW) | Demand (A) | Breakers Used | Status
DP-1 | 208/3/60 | 225 | 42.5 | 0.8 | 34 | 118 | RTU-1, RTU-2, ERV, WH
LP-1 | 120/208 1ph | 125 | 18 | 0.8 | 14.4 | 120 | Units 1xx lighting/recept
LP-2 | 120/208 1ph | 125 | 18 | 0.8 | 14.4 | 120 | Units 2xx lighting/recept
HP-1 | 120/208 1ph | 100 | 12 | 1 | 12 | 100 | Common areas, corridor
FEEDER SIZING
Feeder ID | From | To | Length (m) | Load (A) | Conductor | Conduit | Vdrop (%) | Status
F-001 | MDP | DP-1 | 25 | 118 | 3#2/0 + #6G | 2" EMT | 1.8
F-002 | DP-1 | LP-1 | 15 | 120 | 3#1 + #6G | 1-1/2" EMT | 1.2
F-003 | DP-1 | LP-2 | 15 | 120 | 3#1 + #6G | 1-1/2" EMT | 1.2
F-004 | DP-1 | HP-1 | 10 | 100 | 3#2 + #6G | 1-1/4" EMT | 0.8

## EQUIPMENT
MASTER EQUIPMENT SCHEDULE
Tag | Description | Manufacturer | Model | Capacity | Electrical | Weight (kg) | Dim. L×W×H (mm) | Location | Service Clearance
RTU-1 | Rooftop Unit Units 1xx | Trane | Precedent THC07 | 7.5T / 1500 CFM | 208/3/60 25A | 280 | 1500×1200×1100 | Roof Zone A | 900mm all sides
RTU-2 | Rooftop Unit Units 2xx | Trane | Precedent THC07 | 7.5T / 1500 CFM | 208/3/60 25A | 280 | 1500×1200×1100 | Roof Zone B | 900mm all sides
ERV-1 | Energy Recovery Ventilator | Lifebreath | 1200ERV | 1200 CFM | 120/1/60 8A | 95 | 900×700×1800 | Mech Room 1 | 600mm front
EF-1 | Bath Exhaust Fan | Fantech | RE 6XL | 200 CFM | 120/1/60 3A | 12 | 350×350×300 | Roof | N/A (roof mounted)
WH-1 | Water Heater Units 1xx | Giant | UG-270 | 270L / 150L/h | 240/1/60 18A | 85 | 650Φ×1500 | Mech Room | 600mm front
WH-2 | Water Heater Units 2xx | Giant | UG-270 | 270L / 150L/h | 240/1/60 18A | 85 | 650Φ×1500 | Mech Room | 600mm front

## VALIDATION
AUTOMATED VALIDATION CHECKS
Check ID | Description | Source | Target | Expected | Actual | Status | Action
V-001 | Supply CFM = Return CFM (±10%) | HVAC!F | HVAC!G | Match ±10% |  |  | Adjust return/exhaust to balance
V-002 | Equipment kW → Panel breaker | EQUIPMENT!F | ELECTRICAL!D | All equipment has panel assignment |  | MANUAL | Add missing circuits
V-003 | Panel load ≤ 80% bus | ELECTRICAL!G | ELECTRICAL!C | Demand A ≤ 0.8 × Bus A |  | MANUAL | Reduce load or upsize panel
V-004 | Phase imbalance ≤ 10% | ELECTRICAL!D |  | ≤10% |  | MANUAL | Redistribute loads
V-005 | Duct velocity within limits | HVAC!D |  | Supply ≤1500, Return ≤1200 |  | MANUAL | Upsize duct
V-006 | Fixture units ≤ pipe capacity | PLUMBING!D | PLUMBING!F | Check vs NPC table |  | MANUAL | Upsize pipe
V-007 | Equipment dims ≤ room space | EQUIPMENT!H | ARCH | Coordinated with arch |  | MANUAL | Verify with architectural
V-008 | Assumptions dated | ASSUMPTIONS!A | PROJECT!B13 | Date matches last review |  | MANUAL | Update assumptions

## CAD EXPORT
CAD EXPORT — Ready for AutoCAD Data Link
Copy values only. No formulas. AutoCAD reads this sheet as a linked table.
EQUIPMENT SCHEDULE
Tag | Description | Capacity | Electrical | Location
RTU-1 | Rooftop Unit Units 1xx | 7.5T / 1500 CFM | 208/3/60 25A | Roof Zone A
RTU-2 | Rooftop Unit Units 2xx | 7.5T / 1500 CFM | 208/3/60 25A | Roof Zone B
ERV-1 | Energy Recovery Ventilator | 1200 CFM | 120/1/60 8A | Mech Room 1
EF-1 | Bath Exhaust Fan | 200 CFM | 120/1/60 3A | Roof
WH-1 | Water Heater Units 1xx | 270L / 150L/h | 240/1/60 18A | Mech Room
WH-2 | Water Heater Units 2xx | 270L / 150L/h | 240/1/60 18A | Mech Room
DUCTWORK SUMMARY
Duct ID | Serves | CFM | Size | Notes
M-001 | Units 1xx Supply | 630 | 14"Φ
M-002 | Units 2xx Supply | 630 | 14"Φ
M-003 | Corridors Supply | 150 | 10"Φ
M-R01 | Units 1xx Return | 570 | 14"Φ
M-R02 | Units 2xx Return | 570 | 14"Φ
M-E01 | Bath Exhaust | 100 | 8"Φ
M-E02 | Bath Exhaust | 100 | 8"Φ